OPC/MSEDE Tag Names & Communication

12/1/2022

Rev. 1 ABSTRACT:

This document gives server and sub-server names and all Point-ID and Point Parameter information required to control the MUPP from third-party OPC-compliant software. This information can also enable MUPP control from Excel using MSEDE. Further, this document describes the process that must be carried out in the Experion Station HMI to allow third-party programs to gain control over all MUPP assets required to control the plant.

- Contents

List of Tables	3

List of Figures	3

Document Control and Revision History	4

Definitions	5

1.0	Purpose	6

2.0	Scope	7

3.0	Tables of Parameters	8

4.0	Enabling External Control in Station	12

5.0	Additional Reading	13

List of Tables

Table 1: Document Control and Revision History	4

Table 2: Pilot Plant Server Details.	8

Table 3: Level transmitters with associated point ID and Parameter.	8

Table 4: Flow transmitters with associated point ID and Parameter.	8

Table 5: Temperature transmitters with associated point ID and Parameter.	9

Table 6: Density transmitters with associated point ID and Parameter.	9

Table 7: Pump speed control with associated point ID and Parameter. NOTE: RED TEXT INDICATES A CHANGE SINCE THE LAST REVISION.	9

Table 8: Pump state (ON/OFF) control with associated point ID and Parameter.	10

Table 9: Flow Control Valve position control with associated point ID and Parameter. NOTE: RED TEXT INDICATES A CHANGE SINCE THE LAST REVISION.	10

Table 10: Agitator state (ON/OFF) control with associated point ID and Parameter.	10

Table 11: Solenoid Valve position (OPEN/CLOSED) control with associated point ID and Parameter.	11

Table 3: Recommended further reading and their relevance in the context of this document.	13

# Document Control and Revision History

Table 1: Document Control and Revision History

| Revision | Date | Author(s) | Reviewed by | Comments/Details |
| --- | --- | --- | --- | --- |
| 0 | 2010 | Earl Hopkinson |  | Table of parameters only |
| 1 | 2022 | Nicholas O’Keeffe |  | All sections new except for section 5 which is a modified version of rev0 document. |

# Definitions

| AG | Agitator |
| --- | --- |
| BMP | Ball Mill Pump |
| CRP | Cyclone Recycle Pump |
| CUFP | Cyclone Underflow Pump |
| DT | Density Transmitter |
| EPKS | Experion Process Knowledge System |
| FCV | Flow Control Valve |
| FDP | Feed Disturbance Pump |
| FP | Feed Pump |
| FT | Flow Transmitter |
| HMI | Human Machine Interface |
| LT | Level Transmitter |
| LUP | Lamella Underflow Pump |
| MSEDE | Microsoft Excel Data Exchange |
| MUPP | Murdoch University Pilot Plant |
| NUFP/NTP | Needle Tank Underflow Pump |
| OPC | Open Protocol Communications |
| PP | Product Pump |
| SV | Solenoid Valve |
| TT | Temperature Transmitter |

# Purpose

The purpose of this document is to define details on the parameters required for control of the MUPP via third-party software. It is intended that this document is used to assist users in setting up control strategies using Open Protocol Communications (OPC); as such, it is recommended for use with OPC-compliant software. However, this information can also enable plant control via Microsoft Excel Data Exchange (MSEDE). Several documents are recommended for additional reading in section 6.0, which will help contextualise the information contained in this document, and further clarify the use of the MUPP.

# Scope

This document gives server and sub-server names and all Point-ID and Point Parameter information required to control the MUPP from third-party OPC-compliant software. The Point-ID and Point Parameter information can also enable control using MSEDE. Further, this document describes the process that must be carried out in the Experion Station HMI to allow third-party programs to gain control over the assets described in the following section.

# Tables of Parameters

The proceeding tables show the configuration details of each relevant parameter that can be read-from/written-to using the OPC protocol. Where changes have been enacted since the last revision, the assets and fields in question will be shown in red for clarity. Each table shows the asset in the first column (e.g., a pump, valve or transmitter), the point ID in the second column (synonymous with control modules in EPKS), and the point parameter in the third column. Only the server details (Table 2), Point ID, and Point Parameter (Columns 2 and 3 of Tables 3-11) are required to configure communication via MSEDE or OPC.

Table 2: Pilot Plant Server Details.

| SERVER NAME: | PPServer1 |
| --- | --- |
| EPKS SUB-SERVER: | HWHsc.OPCServer |

NOTE: Sub-server details NOT required for MSEDE, only OPC applications.

Table 3: Level transmitters with associated point ID and Parameter.

| Asset: | Point ID: | Point Parameter: |
| --- | --- | --- |
| LT - 102 | LT_102 | LT_102.PV |
| LT - 122 | LT_122 | LT_122.PV |
| LT - 222 | LT_222 | LT_222.PV |
| LT - 322 | LT_322 | LT_322.PV |
| LT - 501 | LT_501 | LT_501.PV |
| LT - 542 | LT_542 | LT_542.PV |
| LT - 667 | LT_667 | LT_667.PV |

Table 4: Flow transmitters with associated point ID and Parameter.

| Asset: | Point ID: | Point Parameter: |
| --- | --- | --- |
| FT - 148 | FT_148 | FT_148.PV |
| FT - 247 | FT_247 | FT_247.PV |
| FT - 347 | FT_347 | FT_347.PV |
| FT - 363 | FT_363 | FT_363.PV |
| FT - 401 | FT_401 | FT_401.PV |
| FT - 523 | FT_523 | FT_523.PV |
| FT - 569 | FT_569 | FT_569.PV |
| FT - 573 | FT_573 | FT_573.PV |
| FT - 613 | FT_613 | FT_613.PV |
| FT - 687 | FT_687 | FT_687.PV |
| FT - 689 | FT_689 | FT_689.PV |

Table 5: Temperature transmitters with associated point ID and Parameter.

| Asset: | Point ID: | Point Parameter: |
| --- | --- | --- |
| TT - 568 | TT_568 | TT_568.PV |
| TT - 623 | TT_623 | TT_623.PV |
| TT - 643 | TT_643 | TT_643.PV |
| TT - 663 | TT_663 | TT_663.PV |

Table 6: Density transmitters with associated point ID and Parameter.

| Asset: | Point ID: | Point Parameter: |
| --- | --- | --- |
| DT - 103 | DT_103 | DT_103.PV |
| DT - 123 | DT_123 | DT_123.PV |
| DT - 223 | DT_223 | DT_223.PV |
| DT - 323 | DT_323 | DT_323.PV |

Table 7: Pump speed control with associated point ID and Parameter. NOTE: RED TEXT INDICATES A CHANGE SINCE THE LAST REVISION.

| Asset: | Point ID: | Point Parameter: |
| --- | --- | --- |
| BMP | BMP_REF_241-R1A | BMP241_OPC.PV |
| CRP | CRP_REF_341-R1A | CRP341_OPC.PV |
| CUFP | CUFP_REF_361-R1A | CUFP361_OPC.PV |
| FDP | FDP_REF_521-R1A | FDP521_OPC.PV |
| FP | FP_REF_141-R1A | FP141_OPC.PV |
| LUP | LUP_REF_421-R1A | LUP421_OPC.PV |
| NUFP | NTP_REF_561-R1A | NTP561_OPC.PV |
| PP | PP_REF_681-R1A | PP681_OPC.PV |

NOTE: See section 4.0 Enabling External Control in Station for details pertaining to using FCVs in third-party programs.

Table 8: Pump state (ON/OFF) control with associated point ID and Parameter.

| Asset | Point ID: | Point Parameter |
| --- | --- | --- |
| BMP | BMP_OFF_241 | BMP_ON_OFF.PVFL |
| CRP | CRP_OFF_341 | CRP_ON_OFF.PVFL |
| CUFP | CUFP_OFF_361 | CUFP_ON_OFF.PVFL |
| FDP | FDP_OFF_521 | FDP_ON_OFF.PVFL |
| FP | FP_OFF_141 | FP_ON_OFF.PVFL |
| LUFP | LUP_OFF_421 | LUP_ON_OFF.PVFL |
| NUFP | NTP_OFF_561 | NTP_ON_OFF.PVFL |
| PP | PP_OFF_681 | PP_ON_OFF.PVFL |

Table 9: Flow Control Valve position control with associated point ID and Parameter. NOTE: RED TEXT INDICATES A CHANGE SINCE THE LAST REVISION.

| Asset | Point ID: | Point Parameter |
| --- | --- | --- |
| FCV - 541 | FCV_541-R1 | FCV541_OPC.PV |
| FCV - 570 | FCV_570-R1 | FCV570_OPC.PV |
| FCV – 574 *OOC* | FCV_574-R1 | FCV574_OPC.PV |
| FCV – 622 *OOC* | FCV_622-R1 | FCV622_OPC.PV |
| FCV - 642 | FCV_642-R1 | FCV642_OPC.PV |
| FCV - 662 | FCV_662-R1 | FCV662_OPC.PV |
| FCV - 688 | FCV_688-R1 | FCV688_OPC.PV |
| FCV - 690 | FCV_690-R1 | FCV690_OPC.PV |

NOTE: See section 4.0 Enabling External Control in Station for details pertaining to using FCVs in third-party programs.

Table 10: Agitator state (ON/OFF) control with associated point ID and Parameter.

| Asset | Point ID: | Point Parameter |
| --- | --- | --- |
| AG - 101 | AG_101 | AG_ON_OFF.PVFL |
| AG - 121 | AG_OFF_121 | AG_ON_OFF.PVFL |
| AG - 221 | AG_OFF_221 | AG_ON_OFF.PVFL |
| AG - 321 | AG_321 | AG_ON_OFF.PVFL |
| AG - 621 | AG_621 | AG_ON_OFF.PVFL |
| AG - 641 | AG_641 | AG_ON_OFF.PVFL |
| AG - 661 | AG_661 | AG_ON_OFF.PVFL |

NOTE: To use control AGs over EXCEL or OPC, set AGs to program mode in Experion station

Table 11: Solenoid Valve position (OPEN/CLOSED) control with associated point ID and Parameter.

| Asset | Point ID: | Point Parameter |
| --- | --- | --- |
| SV - 104 | SV_104 | B13_4_1.PVFL |
| SV - 105 | SV_105 | B13_4_2.PVFL |
| SV - 124 | SV_124 | B13_4_4.PVFL |
| SV - 125 | SV_125 | B13_4_5.PVFL |
| SV - 614 | SV_614 | B13_5_10.PVFL |
| SV - 615 | SV_615 | B13_5_11.PVFL |
| SV - 616 | SV_616 | B13_5_12.PVFL |
| SV - 691 | SV_691 | B13_6_1.PVFL |
| SV - 692 | SV_692 | B13_6_2.PVFL |
| SV - 693 | SV_693 | B13_6_3.PVFL |

NOTE: To use control SVs over EXCEL or OPC, set SVs to program mode in Experion station

Table 12: Controlled assets OPC routing status associated point ID and Parameter.

| Asset | Point ID: | Point Parameter |
| --- | --- | --- |
| BMP | BMP_REF_241-R1A | OPCenable.PVFL |
| CRP | CRP_REF_341-R1A | OPCenable.PVFL |
| CUFP | CUFP_REF_361-R1A | OPCenable.PVFL |
| FDP | FDP_REF_521-R1A | OPCenable.PVFL |
| FP | FP_REF_141-R1A | OPCenable.PVFL |
| LUFP | LUP_REF_421-R1A | OPCenable.PVFL |
| NUFP | NTP_REF_561-R1A | OPCenable.PVFL |
| PP | PP_REF_681-R1A | OPCenable.PVFL |
| FCV - 541 | FCV_541-R1 | OPCenable.PVFL |
| FCV - 570 | FCV_570-R1 | OPCenable.PVFL |
| FCV – 574 *OOC* | FCV_574-R1 | OPCenable.PVFL |
| FCV – 622 *OOC* | FCV_622-R1 | OPCenable.PVFL |
| FCV - 642 | FCV_642-R1 | OPCenable.PVFL |
| FCV - 662 | FCV_662-R1 | OPCenable.PVFL |
| FCV - 688 | FCV_688-R1 | OPCenable.PVFL |
| FCV - 690 | FCV_690-R1 | OPCenable.PVFL |

# Enabling External Control in Station

For safety purposes, all externally controlled flow controls and pumps (Table 7, Table 9) must be enabled from the EPKS HMI before the program will route externally controlled parameters to the control element. External control of each asset is enabled on a per-controller basis, the process of which is as follows:

- Open the control parameters popup for the relevant plant asset in the MUPP HMI.

- Check the ‘Enable OPC Outer Loop’ tick box (Figure 1).

- Check the ‘Controller Active’ tick box (Figure 1).

NOTE: When controlling the MUPP via OPC it is worthwhile monitoring the status of OPC in EPKS, Table 12 shows the OPC enable status of each of the controlled assets; this parameter is a Boolean value that reads TRUE when control by third-party programs via OPC is being allowed.

Figure 1: Cyclone Underflow Pump popup menu. The red box indicates OPC enable check box, and the green box indicates the controller enable checkbox. Both OPC and Controller enable checkboxes must be checked to allow for MUPP control from a third-party program.

# Additional Reading

Consult Table 13 for recommendations for further reading.

Table 13: Recommended further reading and their relevance in the context of this document.

| Document: | Relevance: |
| --- | --- |
| PP-5001: Operating Pilot Plant via Excel | PP-5001 outlines how to implement parameter control from MATLAB using Excel and Microsoft Excel Data Exchange. |
| PP-5002: Operating Pilot Plant via Station Rev. 1 | PP-5002 gives insight into the operation of the MUPP in Experion Station, including guides on controller configuration. |
| PP-5007: ‘OPCControlTemplateR0’: Use and Function Rev. 0 | PP-5007 outlines how to implement parameter control from MATLAB using the ‘OPCControlTemplateR0’ Program. |