‘PPServer1’ CM Summary

11/23/2022

Revision 0

ABSTRACT:
The purpose of this document is to outline the assortment of active CMs in the MUPP C300 controller. As well as listing the CMs themselves, this document also summarises the purpose and some details of the control modules.

- Contents

1.	Summary of MUPP CMs	1

# Summary of MUPP CMs

| General Info |  |  |  | CM information |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CM | Asset Name | channel input/output | CM description | Indicate Only? | Internal Logic? | Interlocks? | SCM? | Notes |
| 100_CF_01 | Cabinet Cooling Fans | input | Indication state for C300 cabinet cooling fans, output PVFL 100CF01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE |  |
| 100_PS_01 | C300 Top Power Supply | input | Indication state for C300 Top power supply health, output PVFL 100PS01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE |  |
| 100_PS_02 | C300 Bottom Power Supply | input | Indication state for C300 bottom power supply health, output PVFL 100PS02 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE |  |
| 100_TS_01 | C300 Cabinet Temp. | input | Indication state of C300 cabinet temperature, output PVFL 100TS01 indicates temp HIGH/NOT HIGH | TRUE | FALSE | FALSE | FALSE |  |
| 3WV_143 | Three-way valve 143 | input/output | Supply Tank 1, Supply tank 2, Feed Pump to ball mill Control of 3WV-143 | FALSE | TRUE | FALSE | FALSE |  |
| 3WV_368 | Three-way valve 368 | input/output | CUFT, Supply tank 1, supply tank 2 Control of 3WV-368 | FALSE | TRUE | FALSE | FALSE |  |
| 3WV_428 | Three-way valve 428 | input/output | Lamella underflow pump, supply tank 1, supply tank 2 Control of 3WV-428 | FALSE | TRUE | FALSE | FALSE |  |
| 3WV_572 | Three-way valve 572 | input/output | Needle tank underflow pump, supply tank 1, supply tank 2 Control of 3WV-572 | FALSE | TRUE | FALSE | FALSE |  |
| AG_101 | Supply Tank 1 Agitator | output | AG_101 Logic | FALSE | TRUE | FALSE | FALSE |  |
| AG_321 | CUFT Agitator | output | AG_321 Logic | FALSE | TRUE | TRUE | FALSE |  |
| AG_621 | CSTR1 Agitator | output | AG_621 Logic | FALSE | TRUE | TRUE | FALSE |  |
| AG_641 | CSTR2 Agitator | output | AG_641 Logic | FALSE | TRUE | TRUE | FALSE |  |
| AG_661 | CSTR3 Agitator | output | AG_661 Logic | FALSE | TRUE | TRUE | FALSE |  |
| AG_FLT_101 | Supply Tank 1 Agitator | input | Fault status of AG_101, output PVFL AGFLT101 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_121 | Supply Tank 2 Agitator | input | Fault status of AG_121, output PVFL AGFLT121 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_221 | BMT Agitator | input | Fault status of AG_221, output PVFL AGFLT221 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_321 | CUFT Agitator | input | Fault status of AG_321, output PVFL AGFLT321 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_621 | CSTR1 Agitator | input | Fault status of AG_621, output PVFL AGFLT621 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_641 | CSTR2 Agitator | input | Fault status of AG_641, output PVFL AGFLT641 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_FLT_661 | CSTR3 Agitator | input | Fault status of AG_661, output PVFL AGFLT661 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| AG_OFF_121 | Supply Tank 2 Agitator | output | AG_121 Logic | FALSE | TRUE | TRUE | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661 |
| AF_OFF_221 | BMT Agitator | output | AG_221 Logic | FALSE | TRUE | TRUE | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661 |
| AG_RUN_101 | Supply Tank 1 Agitator | input | Indication of agitator state output PVFL AGRUN101 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_121 | Supply Tank 2 Agitator | input | Indication of agitator state output PVFL AGRUN121 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_221 | BMT Agitator | input | Indication of agitator state output PVFL AGRUN221 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_321 | CUFT Agitator | input | Indication of agitator state output PVFL AGRUN321 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_621 | CSTR1 Agitator | input | Indication of agitator state output PVFL AGRUN621 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_641 | CSTR2 Agitator | input | Indication of agitator state output PVFL AGRUN641 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| AG_RUN_661 | CSTR3 Agitator | input | Indication of agitator state output PVFL AGRUN661 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE |  |
| BM_FLT_201 | Ball Mill | input | Indication of ball mill fault state output PVFL BMFLT201 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| BM_G1_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 1) output PVFL BMG1201 indicates positive position POSITION 1/NO POSITION | TRUE | FALSE | FALSE | FALSE |  |
| BM_G2_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 2) output PVFL BMsG2201 indicates positive position POSITION 2/NO POSITION | TRUE | FALSE | FALSE | FALSE | Inconsistant nomenclature of PVFLs for two ball mill guard positions |
| BM_REF_201 | Ball Mill | none (logic only) | Ball Mill logic and control | FALSE | TRUE |  | FALSE |  |
| BM_RUN_201 | Ball Mill | input/output | Ball Mill logic and indication of ball mill state output PVFL BMRUN201 indicates status RUNNING/NOT RUNNING | FALSE | TRUE |  | FALSE |  |
| BM_TANK | Ball Mill Tank | none (logic only) | BMT logic; contains blocks to perform program execution relevent to ball mill page of HMI (304) | FALSE | TRUE |  | FALSE | part of Joshua Dring's thesis |
| BM_TANK_OP | Ball Mill Tank | input/output | cycles the valves, motors, and pumps present on pg 303 of the HMI | FALSE | TRUE |  | TRUE | Automation SCM, part of Joshua Dring's thesis |
| BMP_FLT_241 | Ball Mill Pump | input | indication of fault status of mall mill pump output PVFL BMPFLT241 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| BMP_OFF_241 | Ball Mill Pump | input/output | ball mill pump status logic, determines if BMP is on or off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of BMP, BMT level, and CUFT level. |
| BMP_REF_241-R1A | Ball Mill Pump | none (logic only) | ball mill pump speed reference control. (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| BMP_REF_241_MNTC | Ball Mill Pump | none (logic only) | ball mill pump speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** |
| CA_623 | CSTR1? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !! |
| CA_643 | CSTR2? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !! |
| CA_663 | CSTR3? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !! |
| CM_FF_Test | N/A | N/A | Foundation fieldbus example CM | FALSE | FALSE | FALSE | FALSE | FOUNDATION FIELDBUS EXAMPLE CM |
| CRP_FLT_341 | Cyclone Recycle Pump | input | indication of fault status of cyclone recycle pump output PVFL CRPFLT341 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| CRP_OFF_341 | Cyclone Recycle Pump | input/output | cyclone recycle pump status logic, determines if CRP is on/off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of CRP, 3WV-368 position, supply tank levels, and CUFT level. |
| CRP_REF_341-R1A | Cyclone Recycle Pump | none (logic only) | CRP speed reference control. (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| CRP_REF_341_MNTC | Cyclone Recycle Pump | none (logic only) | CRP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** |
| CSTR_TANKS | CSTR bank | none (logic only) | CSTR bank logic; contains blocks to perform the program execution relevent to CSTR page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis |
| CSTR_TANKS_OP | CSTR bank | input/output | cycles the valves, motors, and pumps present on pg 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis |
| CUF_TANK | Cyclone Underflow Tank | none (logic only) | CUFT logic, contains blocks to perform the program execution relevent to cyclone page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis |
| CUF_TANK_OP | Cyclone Underflow Tank | input/output | cycles the valves, pumps, and motors present on og 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis |
| CUFP_FLT_361 | Cyclone Underflow Pump | input | indication of fault status of CUFP. Output PVFL CUFPFLT361 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| CUFP_OFF_361 | Cyclone Underflow Pump | input/output | cyclone underflow pump status logic, determines if CUFP is on/off | FALSE | TRUE | TRUE | FALSE | ** Contains configurable interlock PVs relating to flow out of CUFP, BMT lavel, and CUFT level. **possible irrational interlock** |
| CUFP_REF_361-R1A | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| CUP_REF_361_MNTC | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** inconsistant nomenclature of CUFP vs CUP in other cyclone underflow pump CMs |
| DP_FLT_611 | Dye Pump | input | Indication of fault status of dye pump output PVFL DPFLT611 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| DP_OFF_611 | Dye Pump | input/output | dye pump status logic, determines if DP IS ON/OFF | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks relating to DT>CSTR SVs SV_614,615,616, and flow out of DP. |
| DP_REF_611 | Dye Pump | none (logic only) | DP speed reference control | FALSE | TRUE | FALSE | FALSE | Density transmitters |
| DT_103 | Supply Tank 1 | input | Data acquisition of density transmitter on supply tank 1 | FALSE | TRUE | FALSE | FALSE | Density transmitters |
| DT_123 | Supply Tank 2 | input | Data acquisition of density transmitter on supply tank 2 | FALSE | TRUE | FALSE | FALSE | Density transmitters |
| DT_223 | Ball Mill Tank | input | Data acquisition of density transmitter on ball mill tank | FALSE | TRUE | FALSE | FALSE | Density transmitters |
| DT_323 | Cyclone Underflow Tank | input | Data acquisition of density transmitter on CUFT | FALSE | TRUE | FALSE | FALSE | Density transmitters |
| FCV_541-R1A | FCV (NLT input) | output | nonlinear tank input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_541_MNTC | FCV (NLT input) | output | nonlinear tank input FCV control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** FCVs inconsistant nomenclature with other maintenance mode controls |
| FCV_570-R1A | FCV (NT to CSTR1) | output | needle tank to cstr1 FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_571-R1A | FCV (NT to STs) | output | Needle tank to supply tanks FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_574-R1A | FCV (NT to BM) | output | needle tank to ball mill FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_622-R1A | FCV (Steam to CSTR1) | output | CSTR1 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_642-R1A | FCV (Steam to CSTR2) | output | CSTR2 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_662-R1A | FCV (Steam to CSTR3) | output | CSTR3 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_688-R1A | FCV (Prod. From PP) | output | product output (from CSTR3 PP) FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FCV_690-R1A | FCV (Reflux from PP) | output | reflux from CSTR3 to CSTR1,2,3 FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision |
| FDP_FLT_521 | Flow Disturbance Pump | input | indication of fault status of flow disturbance pump output PVFL FDPFLT521 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| FDP_OFF_521 | Flow Disturbance Pump | input/output | flow disturbance pump status logic, determines if FDP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FDP, NT level and NLT level. |
| FDP_REF_521-R1A | Flow Disturbance Pump | none (logic only) | FDP speed reference control | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| FDP_REF_521_MNTC | Flow Disturbance Pump | none (logic only) | FDP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** |
| FP_FLT_141 | Feed Pump | input | indication of fault status of feed pump output PVFL FPFLT141 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| FP_OFF_141 | Feed Pump | input/output | feed pump status logic, determines if FP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FP, supply tank 1 level and supply tank 2 level. |
| FP_REF_141-R1A | Feed Pump | none (logic only) | FP speed reference control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| FP_REF_141_MNTC | Feed Pump | none (logic only) | FP speed reference control (Alternative) Maintenance mode | FALSE | TRUE | FALSE | FALSE | ** |
| FT_148 | FT (FP to BM) | input | feed pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_247 | FT (BMP to Cyclone) | input | ball mill pump to hydrocyclone flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_347 | FT (CRP to BM) | input | cyclone recycle pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_363 | FT (CUFP to STs) | input | cyclone underflow pump to storage tanks flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable !!! Possible mistake on Hopkinson P&ID, unable to determin if FT_363 is CUFP to STs, or CRP to BM |
| FT_401 | FT (Lamella to NT) | input | lamella overflow to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_523 | FT (FDP to NT) | input | flow disturbance pump to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_569 | FT (NUFP to CSTR1) | input | needle tank underflow pump to cstr1 flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_573 | FT (NUFP to BM) | input | needle tank underflow pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented |
| FT_613 | FT (DP to CSTR bank) | input | dye pump to cstr bank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented |
| FT_687 | FT (PP to Output) | input | product pump to output drain flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable |
| FT_689 | FT (PP to CSTR reflux) | input | product pump to cstr reflux piping flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented |
| I/O | N/A | N/A | input/output read/write? | FALSE | TRUE | FALSE | FALSE |  |
| LT_102 | LT (Storage Tank 1) | input | storage tank 1 level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_122 | LT (Storage Tank 2) | input | storage tank 2 level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_222 | LT (BMT) | input | Ball mill tank level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_322 | LT (CUFT) | input | cyclone underflow tank level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_422 | Bool (LL/HH) Lamella? | input | unknown (no commenting), presumed to be lamella LL and HH sensors. See use in LUP_OFF_421 | TRUE | FALSE | FALSE | FALSE | !! |
| LT_501 | LT (NT) | input | needle tank level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_542 | LT (NLT) | input | nonlinear tank level transmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LT_667 | LT (CSTR3) | input | cstr3 tank level treansmitter read | FALSE | TRUE | FALSE | FALSE |  |
| LUP_FLT_421 | Lamella underflow pump | input | indication of fault status of lamella underflow pump output PVFL LUPFLT421 indicates FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| LUP_OFF_421 | Lamella underflow pump | output | lamella underflow pump status logic, determines if LUP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to lamella LL alarm |
| LUP_REF_421-R1A | Lamella underflow pump | none (logic only) | LUP reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| LUP_RUN_421 | Lamella underflow pump | input | indication of LUP state output PVFL LUPRUN421 indicates status ON/OFF | TRUE | FALSE | FALSE | FALSE |  |
| MAINTENANCE | N/A | N/A | Part of automated maintenance program, storage of SCM PVs/PVFLs | FALSE | FALSE | FALSE | FALSE | variable storage for SCMs, part of Dring's thesis |
| MS_100 | Maintenance Switch | input | Maintenance switch read, activates maintenance mode output PVFL MS_100 pulses to initiate MM | FALSE | TRUE | FALSE | FALSE | more or less indicate only, activates Dring's maintenance mode |
| NT_TANKS | NLT/NT | none (logic only) | contains logic to perform execution of program related to NT page | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis comments say related to cyclone page (305) however logic indicates its related to NT/NLTs |
| NT_TANKS_OP | NLT/NT | none (logic only) | cycles the valves, pumps, and motors present on og 305 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis |
| NTP_FLT_561 | Needle Tank Underflow Pump | input | indication of fault status of needle tank underflow pump output PVFL NTPFLT561 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| NTP_OFF_561 | Needle Tank Underflow Pump | input/output | needle tank underflow pump state logic, determines if NTP is on/off | FALSE | TRUE | TRUE | FALSE | **contains configurable interlocks relating to flow from NTP to BMT and CSTR1, NT Level, CSTR3 level **possible irrational interlock** |
| NTP_REF_561-R1A | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| NTP_REF_561_MNTC | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** |
| OneWireless_CM | N/A | N/A | Handles Wireless comms with Honeywell VIA Modbus TCP/IP | FALSE | TRUE | FALSE | FALSE | wireless comms |
| OPERATION | N/A | N/A | Uncommented, cruicial to plant operation, allows on state of all pumps, sv's, agitators etc. | FALSE | TRUE | FALSE | FALSE | !! |
| PC3_11_WD1 | N/A | N/A | unknown (uncommented) | FALSE | FALSE | FALSE | FALSE | !!! Possibly unused |
| PID10_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID10_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID11_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID11_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID12_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID12_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID13_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID13_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID14_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID14_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID15_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID15_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID16_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID16_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID17_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID17_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID18_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !! |
| PID19_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID19_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID1_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID1_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID20_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !! |
| PID2_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !! |
| PID3_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID3_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID4_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID4_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID5_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID5_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID6_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID6_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID7_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID7_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID8_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID8_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID9_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID9_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PID_PvSp_ARRAY-R1A | N/A | N/A | Stores variable arrays for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PP_FLT_681 | Product Pump | input | indication of fault status of product pump output PVFL PPFLT681 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE |  |
| PP_OFF_681 | Product Pump | input/output | product pump state logic, determines if PP is on/off | FALSE | TRUE | TRUE | FALSE | ** contains configurable interlocks relating to flow out of PP via FT_687,689, CSTR3 level, and a combined valve limit imposed on FCV_688,690. **possible irrational interlock** |
| PP_REF_681-R1A | Product Pump | none (logic only) | Product pump reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision |
| PP_REF_681_MNTC | Product Pump | none (logic only) | Product pump reference speed control (Alternatice) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** |
| PPSTLevels1__WD1 | N/A | N/A | unknown (uncommented) |  |  |  |  | !!! Possibly unused |
| PT_669 | Steam Pressure Trans. | input | Data Acquisition for pressure transmitter on steam line | FALSE | TRUE | FALSE | FALSE |  |
| SPARE | N/A | none (logic only) | Labelled as spare PID action control flow | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| ST_TANKS | Storage Tanks | none (logic only) | contains logic to perform execution of program related to Storage tank page (302) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis |
| ST_TANKS_OP | Storage Tanks | none (logic only) | cycles the valves, motors and pumps associated with first section of the plant (HMI pp 302) | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis |
| SV_104 | Storage Tank 1 | output | SV from water addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level |
| SV_105 | Storage Tank 1 | output | SV from Air addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level |
| SV_124 | Storage Tank 2 | output | SV from water addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level |
| SV_125 | Storage Tank2 | output | SV from Air addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level |
| SV_614 | CSTR3 | output | SV from dye pump to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level |
| SV_615 | CSTR2 | output | SV from dye pump to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level |
| SV_616 | CSTR1 | output | SV from dye pump to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level |
| SV_691 | CSTR3 | output | SV from product pump reflux to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level |
| SV_692 | CSTR2 | output | SV from product pump reflux to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level |
| SV_693 | CSTR1 | output | SV from product pump reflux to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level |
| SV_AIR | AIR System | output | Determines if AIR supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out |
| SV_STEAM | STEAM System | output | Determines if STEAM supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out |
| SV_WATER | WATER System | output | Determines if WATER supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out |
| TempPC1_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TempPC2_2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TempPC2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TempPC2OP3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TempPC2OP_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TmpLevPC4_3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TmpLevPC5_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TmpLevPC6_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TmpLvlPC3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused |
| TRBSHT_OP | System Control | none (logic only) | Changes all mode attributes of each device control to program | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis |
| TT_568 | CSTR1 | input | Data Acquisition from temperature transmitter on CSTR1 feed inlet | FALSE | TRUE | FALSE | FALSE |  |
| TT_623 | CSTR1 | input | Data Acquisition from temp trans. Inside CSTR1 | FALSE | TRUE | FALSE | FALSE |  |
| TT_643 | CSTR2 | input | Data Acquisition from temp trans. Inside CSTR2 | FALSE | TRUE | FALSE | FALSE |  |
| TT_663 | CSTR3 | input | Data Acquisition from temp trans. Inside CSTR3 | FALSE | TRUE | FALSE | FALSE |  |
| WARN_BUZZ | Warning Buzzer | output | Control of warning buzzer | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant |
| WARN_LGHT | Warning Light | input | control of warning light allegedly | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant |