## Rev0
General Info |  |  |  | CM information
CM | Asset Name | channel input/output | CM description | Indicate Only? | Internal Logic? | Interlocks? | SCM? | Notes
100_CF_01 | Cabinet Cooling Fans | input | Indication state for C300 cabinet cooling fans, output PVFL 100CF01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_PS_01 | C300 Top Power Supply | input | Indication state for C300 Top power supply health, output PVFL 100PS01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_PS_02 | C300 Bottom Power Supply | input | Indication state for C300 bottom power supply health, output PVFL 100PS02 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_TS_01 | C300 Cabinet Temp. | input | Indication state of C300 cabinet temperature, output PVFL 100TS01 indicates temp HIGH/NOT HIGH | TRUE | FALSE | FALSE | FALSE
3WV_143 | Three-way valve 143 | input/output | Supply Tank 1, Supply tank 2, Feed Pump to ball mill Control of 3WV-143 | FALSE | TRUE |  | FALSE
3WV_368 | Three-way valve 368 | input/output | CUFT, Supply tank 1, supply tank 2 Control of 3WV-368 | FALSE | TRUE |  | FALSE
3WV_428 | Three-way valve 428 | input/output | Lamella underflow pump, supply tank 1, supply tank 2 Control of 3WV-428 | FALSE | TRUE |  | FALSE
3WV_572 | Three-way valve 572 | input/output | Needle tank underflow pump, supply tank 1, supply tank 2 Control of 3WV-572 | FALSE | TRUE |  | FALSE
AG_101 | Supply Tank 1 Agitator | output | AG_101 Logic | FALSE | TRUE |  | FALSE
AG_321 | CUFT Agitator | output | AG_321 Logic | FALSE | TRUE |  | FALSE
AG_621 | CSTR1 Agitator | output | AG_621 Logic | FALSE | TRUE |  | FALSE
AG_641 | CSTR2 Agitator | output | AG_641 Logic | FALSE | TRUE |  | FALSE
AG_661 | CSTR3 Agitator | output | AG_661 Logic | FALSE | TRUE |  | FALSE
AG_FLT_101 | Supply Tank 1 Agitator | input | Fault status of AG_101, output PVFL AGFLT101 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_121 | Supply Tank 2 Agitator | input | Fault status of AG_121, output PVFL AGFLT121 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_221 | BMT Agitator | input | Fault status of AG_221, output PVFL AGFLT221 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_321 | CUFT Agitator | input | Fault status of AG_321, output PVFL AGFLT321 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_621 | CSTR1 Agitator | input | Fault status of AG_621, output PVFL AGFLT621 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_641 | CSTR2 Agitator | input | Fault status of AG_641, output PVFL AGFLT641 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_661 | CSTR3 Agitator | input | Fault status of AG_661, output PVFL AGFLT661 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_OFF_121 | Supply Tank 2 Agitator | output | AG_121 Logic | FALSE | TRUE |  | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661
AF_OFF_221 | BMT Agitator | output | AG_221 Logic | FALSE | TRUE |  | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661
AG_RUN_101 | Supply Tank 1 Agitator | input | Indication of agitator state output PVFL AGRUN101 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_121 | Supply Tank 2 Agitator | input | Indication of agitator state output PVFL AGRUN121 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_221 | BMT Agitator | input | Indication of agitator state output PVFL AGRUN221 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_321 | CUFT Agitator | input | Indication of agitator state output PVFL AGRUN321 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_621 | CSTR1 Agitator | input | Indication of agitator state output PVFL AGRUN621 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_641 | CSTR2 Agitator | input | Indication of agitator state output PVFL AGRUN641 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_661 | CSTR3 Agitator | input | Indication of agitator state output PVFL AGRUN661 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
BM_FLT_201 | Ball Mill | input | Indication of ball mill fault state output PVFL BMFLT201 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
BM_G1_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 1) output PVFL BMG1201 indicates positive position POSITION 1/NO POSITION | TRUE | FALSE | FALSE | FALSE
BM_G2_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 2) output PVFL BMsG2201 indicates positive position POSITION 2/NO POSITION | TRUE | FALSE | FALSE | FALSE | Inconsistant nomenclature of PVFLs for two ball mill guard positions
BM_REF_201 | Ball Mill | none (logic only) | Ball Mill logic and control | FALSE | TRUE |  | FALSE
BM_RUN_201 | Ball Mill | input/output | Ball Mill logic and indication of ball mill state output PVFL BMRUN201 indicates status RUNNING/NOT RUNNING | FALSE | TRUE |  | FALSE
BM_TANK | Ball Mill Tank | none (logic only) | BMT logic; contains blocks to perform program execution relevent to ball mill page of HMI (304) | FALSE | TRUE |  | FALSE | part of Joshua Dring's thesis
BM_TANK_OP | Ball Mill Tank | input/output | cycles the valves, motors, and pumps present on pg 303 of the HMI | FALSE | TRUE |  | TRUE | Automation SCM, part of Joshua Dring's thesis
BMP_FLT_241 | Ball Mill Pump | input | indication of fault status of mall mill pump output PVFL BMPFLT241 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
BMP_OFF_241 | Ball Mill Pump | input/output | ball mill pump status logic, determines if BMP is on or off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of BMP, BMT level, and CUFT level.
BMP_REF_241 | Ball Mill Pump | none (logic only) | ball mill pump speed reference control. | FALSE | TRUE |  | FALSE | **
BMP_REF_241_MNTC | Ball Mill Pump | none (logic only) | ball mill pump speed reference control (Alternative) Maintenance Mode | FALSE | TRUE |  | FALSE | **
CA_623 | CSTR1? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CA_643 | CSTR2? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CA_663 | CSTR3? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CM_FF_Test | N/A | N/A | Foundation fieldbus example CM | FALSE | FALSE | FALSE | FALSE | FOUNDATION FIELDBUS EXAMPLE CM
CRP_FLT_341 | Cyclone Recycle Pump | input | indication of fault status of cyclone recycle pump output PVFL CRPFLT341 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
CRP_OFF_341 | Cyclone Recycle Pump | input/output | cyclone recycle pump status logic, determines if CRP is on/off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of CRP, 3WV-368 position, supply tank levels, and CUFT level.
CRP_REF_341 | Cyclone Recycle Pump | none (logic only) | CRP speed reference control. | FALSE | TRUE | FALSE | FALSE | **
CRP_REF_341_MNTC | Cyclone Recycle Pump | none (logic only) | CRP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
CSTR_TANKS | CSTR bank | none (logic only) | CSTR bank logic; contains blocks to perform the program execution relevent to CSTR page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
CSTR_TANKS_OP | CSTR bank | input/output | cycles the valves, motors, and pumps present on pg 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
CUF_TANK | Cyclone Underflow Tank | none (logic only) | CUFT logic, contains blocks to perform the program execution relevent to cyclone page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
CUF_TANK_OP | Cyclone Underflow Tank | input/output | cycles the valves, pumps, and motors present on og 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
CUFP_FLT_361 | Cyclone Underflow Pump | input | indication of fault status of CUFP. Output PVFL CUFPFLT361 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
CUFP_OFF_361 | Cyclone Underflow Pump | input/output | cyclone underflow pump status logic, determines if CUFP is on/off | FALSE | TRUE | TRUE | FALSE | ** Contains configurable interlock PVs relating to flow out of CUFP, BMT lavel, and CUFT level. **possible irrational interlock**
CUP_REF_361 | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control | FALSE | TRUE | FALSE | FALSE | ** inconsistant nomenclature of CUFP vs CUP in other cyclone underflow pump CMs
CUP_REF_361_MNTC | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** inconsistant nomenclature of CUFP vs CUP in other cyclone underflow pump CMs
DP_FLT_611 | Dye Pump | input | Indication of fault status of dye pump output PVFL DPFLT611 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
DP_OFF_611 | Dye Pump | input/output | dye pump status logic, determines if DP IS ON/OFF | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks relating to DT>CSTR SVs SV_614,615,616, and flow out of DP.
DP_REF_611 | Dye Pump | none (logic only) | DP speed reference control | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_103 | Supply Tank 1 | input | Data acquisition of density transmitter on supply tank 1 | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_123 | Supply Tank 2 | input | Data acquisition of density transmitter on supply tank 2 | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_223 | Ball Mill Tank | input | Data acquisition of density transmitter on ball mill tank | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_323 | Cyclone Underflow Tank | input | Data acquisition of density transmitter on CUFT | FALSE | TRUE | FALSE | FALSE | Density transmitters
FCV_541 | FCV (NLT input) | output | nonlinear tank input FCV control | FALSE | TRUE | TRUE | FALSE | ** FCVs
FCV_541_MNTC | FCV (NLT input) | output | nonlinear tank input FCV control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** FCVs inconsistant nomenclature with other maintenance mode controls
FCV_570 | FCV (NT to CSTR1) | output | needle tank to cstr1 FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_571 | FCV (NT to STs) | output | Needle tank to supply tanks FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_574 | FCV (NT to BM) | output | needle tank to ball mill FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_622 | FCV (Steam to CSTR1) | output | CSTR1 steam input FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_642 | FCV (Steam to CSTR2) | output | CSTR2 steam input FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_662 | FCV (Steam to CSTR3) | output | CSTR3 steam input FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_688 | FCV (Prod. From PP) | output | product output (from CSTR3 PP) FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FCV_690 | FCV (Reflux from PP) | output | reflux from CSTR3 to CSTR1,2,3 FCV control | FALSE | TRUE | TRUE | FALSE | FCVs
FDP_FLT_521 | Flow Disturbance Pump | input | indication of fault status of flow disturbance pump output PVFL FDPFLT521 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
FDP_OFF_521 | Flow Disturbance Pump | input/output | flow disturbance pump status logic, determines if FDP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FDP, NT level and NLT level.
FDP_REF_521 | Flow Disturbance Pump | none (logic only) | FDP speed reference control | FALSE | TRUE | FALSE | FALSE | **
FDP_REF_521_MNTC | Flow Disturbance Pump | none (logic only) | FDP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
FP_FLT_141 | Feed Pump | input | indication of fault status of feed pump output PVFL FPFLT141 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
FP_OFF_141 | Feed Pump | input/output | feed pump status logic, determines if FP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FP, supply tank 1 level and supply tank 2 level.
FP_REF_141 | Feed Pump | none (logic only) | FP speed reference control | FALSE | TRUE | FALSE | FALSE | **
FP_REF_141_MNTC | Feed Pump | none (logic only) | FP speed reference control (Alternative) Maintenance mode | FALSE | TRUE | FALSE | FALSE | **
FT_148 | FT (FP to BM) | input | feed pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_247 | FT (BMP to Cyclone) | input | ball mill pump to hydrocyclone flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_347 | FT (CRP to BM) | input | cyclone recycle pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_363 | FT (CUFP to STs) | input | cyclone underflow pump to storage tanks flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable !!! Possible mistake on Hopkinson P&ID, unable to determin if FT_363 is CUFP to STs, or CRP to BM
FT_401 | FT (Lamella to NT) | input | lamella overflow to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_523 | FT (FDP to NT) | input | flow disturbance pump to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_569 | FT (NUFP to CSTR1) | input | needle tank underflow pump to cstr1 flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_573 | FT (NUFP to BM) | input | needle tank underflow pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
FT_613 | FT (DP to CSTR bank) | input | dye pump to cstr bank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
FT_687 | FT (PP to Output) | input | product pump to output drain flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_689 | FT (PP to CSTR reflux) | input | product pump to cstr reflux piping flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
I/O | N/A | N/A | input/output read/write? | FALSE | TRUE | FALSE | FALSE
LT_102 | LT (Storage Tank 1) | input | storage tank 1 level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_122 | LT (Storage Tank 2) | input | storage tank 2 level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_222 | LT (BMT) | input | Ball mill tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_322 | LT (CUFT) | input | cyclone underflow tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_422 | Bool (LL/HH) Lamella? | input | unknown (no commenting), presumed to be lamella LL and HH sensors. See use in LUP_OFF_421 | TRUE | FALSE | FALSE | FALSE | !!
LT_501 | LT (NT) | input | needle tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_542 | LT (NLT) | input | nonlinear tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_667 | LT (CSTR3) | input | cstr3 tank level treansmitter read | FALSE | TRUE | FALSE | FALSE
LUP_FLT_421 | Lamella underflow pump | input | indication of fault status of lamella underflow pump output PVFL LUPFLT421 indicates FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
LUP_OFF_421 | Lamella underflow pump | output | lamella underflow pump status logic, determines if LUP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to lamella LL alarm
LUP_REF_421 | Lamella underflow pump | none (logic only) | LUP reference speed control | FALSE | TRUE | FALSE | FALSE
LUP_RUN_421 | Lamella underflow pump | input | indication of LUP state output PVFL LUPRUN421 indicates status ON/OFF | TRUE | FALSE | FALSE | FALSE
MAINTENANCE | N/A | N/A | Part of automated maintenance program, storage of SCM PVs/PVFLs | FALSE | FALSE | FALSE | FALSE | variable storage for SCMs, part of Dring's thesis
MS_100 | Maintenance Switch | input | Maintenance switch read, activates maintenance mode output PVFL MS_100 pulses to initiate MM | FALSE | TRUE | FALSE | FALSE | more or less indicate only, activates Dring's maintenance mode
NT_TANKS | NLT/NT | none (logic only) | contains logic to perform execution of program related to NT page | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis comments say related to cyclone page (305) however logic indicates its related to NT/NLTs
NT_TANKS_OP | NLT/NT | none (logic only) | cycles the valves, pumps, and motors present on og 305 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
NTP_FLT_561 | Needle Tank Underflow Pump | input | indication of fault status of needle tank underflow pump output PVFL NTPFLT561 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
NTP_OFF_561 | Needle Tank Underflow Pump | input/output | needle tank underflow pump state logic, determines if NTP is on/off | FALSE | TRUE | TRUE | FALSE | **contains configurable interlocks relating to flow from NTP to BMT and CSTR1, NT Level, CSTR3 level **possible irrational interlock**
NTP_REF_561 | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control | FALSE | TRUE | FALSE | FALSE | **
NTP_REF_561_MNTC | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
OneWireless_CM | N/A | N/A | Handles Wireless comms with Honeywell VIA Modbus TCP/IP | FALSE | TRUE | FALSE | FALSE | wireless comms
OPERATION | N/A | N/A | Uncommented, cruicial to plant operation, allows on state of all pumps, sv's, agitators etc. | FALSE | TRUE | FALSE | FALSE | !!
PC3_11_WD1 | N/A | N/A | unknown (uncommented) | FALSE | FALSE | FALSE | FALSE | !!! Possibly unused
PID_10_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_11_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_12_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_13_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_14_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_15_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_16_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_17_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_18_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_19_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_1_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_20_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_2_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_3_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_4_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_5_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_6_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_7_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_8_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_9_PV_SELECT | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PID_PV_ARRAY | N/A | N/A | part of current PID "configuration" method [uncommented] | FALSE | TRUE | FALSE | FALSE | !!
PP_FLT_681 | Product Pump | input | indication of fault status of product pump output PVFL PPFLT681 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
PP_OFF_681 | Product Pump | input/output | product pump state logic, determines if PP is on/off | FALSE | TRUE | TRUE | FALSE | ** contains configurable interlocks relating to flow out of PP via FT_687,689, CSTR3 level, and a combined valve limit imposed on FCV_688,690. **possible irrational interlock**
PP_REF_681 | Product Pump | none (logic only) | Product pump reference speed control | FALSE | TRUE | FALSE | FALSE | **
PP_REF_681_MNTC | Product Pump | none (logic only) | Product pump reference speed control (Alternatice) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
PPSTLevels1__WD1 | N/A | N/A | unknown (uncommented) |  |  |  |  | !!! Possibly unused
PT_669 | Steam Pressure Trans. | input | Data Acquisition for pressure transmitter on steam line | FALSE | TRUE | FALSE | FALSE
SPARE | N/A | none (logic only) | Labelled as spare PID action control flow | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
ST_TANKS | Storage Tanks | none (logic only) | contains logic to perform execution of program related to Storage tank page (302) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
ST_TANKS_OP | Storage Tanks | none (logic only) | cycles the valves, motors and pumps associated with first section of the plant (HMI pp 302) | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
SV_104 | Storage Tank 1 | output | SV from water addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level
SV_105 | Storage Tank 1 | output | SV from Air addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level
SV_124 | Storage Tank 2 | output | SV from water addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level
SV_125 | Storage Tank2 | output | SV from Air addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level
SV_614 | CSTR3 | output | SV from dye pump to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level
SV_615 | CSTR2 | output | SV from dye pump to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_616 | CSTR1 | output | SV from dye pump to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_691 | CSTR3 | output | SV from product pump reflux to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level
SV_692 | CSTR2 | output | SV from product pump reflux to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_693 | CSTR1 | output | SV from product pump reflux to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_AIR | AIR System | output | Determines if AIR supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
SV_STEAM | STEAM System | output | Determines if STEAM supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
SV_WATER | WATER System | output | Determines if WATER supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
TempPC1_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2_2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2OP3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2OP_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC4_3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC5_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC6_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLvlPC3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TRBSHT_OP | System Control | none (logic only) | Changes all mode attributes of each device control to program | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
TT_568 | CSTR1 | input | Data Acquisition from temperature transmitter on CSTR1 feed inlet | FALSE | TRUE | FALSE | FALSE
TT_623 | CSTR1 | input | Data Acquisition from temp trans. Inside CSTR1 | FALSE | TRUE | FALSE | FALSE
TT_643 | CSTR2 | input | Data Acquisition from temp trans. Inside CSTR2 | FALSE | TRUE | FALSE | FALSE
TT_663 | CSTR3 | input | Data Acquisition from temp trans. Inside CSTR3 | FALSE | TRUE | FALSE | FALSE
WARN_BUZZ | Warning Buzzer | output | Control of warning buzzer | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant
WARN_LGHT | Warning Light | input | control of warning light allegedly | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant
Z_CM_FOS | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
Z_CM_LOGIC | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
Z_CM_MULT | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_CM_SIMON | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_CM_SIMON_FOS | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_CM_SIMON_PID | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_dp_flagtest | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_dp_fos | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_dp_fos_1 | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_dp_fos_model | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_SIMON_FLAG | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_SIMON_FOSPID | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused
ZZZ_SIMON_SCM | N/A | N/A | unrelated to PP |  |  |  |  | !!! Possibly unused

## Rev1
General Info |  |  |  | CM information
CM | Asset Name | channel input/output | CM description | Indicate Only? | Internal Logic? | Interlocks? | SCM? | Notes
100_CF_01 | Cabinet Cooling Fans | input | Indication state for C300 cabinet cooling fans, output PVFL 100CF01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_PS_01 | C300 Top Power Supply | input | Indication state for C300 Top power supply health, output PVFL 100PS01 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_PS_02 | C300 Bottom Power Supply | input | Indication state for C300 bottom power supply health, output PVFL 100PS02 indicates health HEALTHY/NOT HEALTHY | TRUE | FALSE | FALSE | FALSE
100_TS_01 | C300 Cabinet Temp. | input | Indication state of C300 cabinet temperature, output PVFL 100TS01 indicates temp HIGH/NOT HIGH | TRUE | FALSE | FALSE | FALSE
3WV_143 | Three-way valve 143 | input/output | Supply Tank 1, Supply tank 2, Feed Pump to ball mill Control of 3WV-143 | FALSE | TRUE | FALSE | FALSE
3WV_368 | Three-way valve 368 | input/output | CUFT, Supply tank 1, supply tank 2 Control of 3WV-368 | FALSE | TRUE | FALSE | FALSE
3WV_428 | Three-way valve 428 | input/output | Lamella underflow pump, supply tank 1, supply tank 2 Control of 3WV-428 | FALSE | TRUE | FALSE | FALSE
3WV_572 | Three-way valve 572 | input/output | Needle tank underflow pump, supply tank 1, supply tank 2 Control of 3WV-572 | FALSE | TRUE | FALSE | FALSE
AG_101 | Supply Tank 1 Agitator | output | AG_101 Logic | FALSE | TRUE | FALSE | FALSE
AG_321 | CUFT Agitator | output | AG_321 Logic | FALSE | TRUE | TRUE | FALSE
AG_621 | CSTR1 Agitator | output | AG_621 Logic | FALSE | TRUE | TRUE | FALSE
AG_641 | CSTR2 Agitator | output | AG_641 Logic | FALSE | TRUE | TRUE | FALSE
AG_661 | CSTR3 Agitator | output | AG_661 Logic | FALSE | TRUE | TRUE | FALSE
AG_FLT_101 | Supply Tank 1 Agitator | input | Fault status of AG_101, output PVFL AGFLT101 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_121 | Supply Tank 2 Agitator | input | Fault status of AG_121, output PVFL AGFLT121 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_221 | BMT Agitator | input | Fault status of AG_221, output PVFL AGFLT221 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_321 | CUFT Agitator | input | Fault status of AG_321, output PVFL AGFLT321 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_621 | CSTR1 Agitator | input | Fault status of AG_621, output PVFL AGFLT621 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_641 | CSTR2 Agitator | input | Fault status of AG_641, output PVFL AGFLT641 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_FLT_661 | CSTR3 Agitator | input | Fault status of AG_661, output PVFL AGFLT661 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
AG_OFF_121 | Supply Tank 2 Agitator | output | AG_121 Logic | FALSE | TRUE | TRUE | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661
AF_OFF_221 | BMT Agitator | output | AG_221 Logic | FALSE | TRUE | TRUE | FALSE | Inconsistant nomenclature of CMs, should follow AG_101,321,621,641,661
AG_RUN_101 | Supply Tank 1 Agitator | input | Indication of agitator state output PVFL AGRUN101 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_121 | Supply Tank 2 Agitator | input | Indication of agitator state output PVFL AGRUN121 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_221 | BMT Agitator | input | Indication of agitator state output PVFL AGRUN221 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_321 | CUFT Agitator | input | Indication of agitator state output PVFL AGRUN321 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_621 | CSTR1 Agitator | input | Indication of agitator state output PVFL AGRUN621 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_641 | CSTR2 Agitator | input | Indication of agitator state output PVFL AGRUN641 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
AG_RUN_661 | CSTR3 Agitator | input | Indication of agitator state output PVFL AGRUN661 indicates status ACTIVE/INACTIVE | TRUE | FALSE | FALSE | FALSE
BM_FLT_201 | Ball Mill | input | Indication of ball mill fault state output PVFL BMFLT201 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
BM_G1_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 1) output PVFL BMG1201 indicates positive position POSITION 1/NO POSITION | TRUE | FALSE | FALSE | FALSE
BM_G2_201 | Ball Mill Guard | input | Indication of ball mill guard position (position 2) output PVFL BMsG2201 indicates positive position POSITION 2/NO POSITION | TRUE | FALSE | FALSE | FALSE | Inconsistant nomenclature of PVFLs for two ball mill guard positions
BM_REF_201 | Ball Mill | none (logic only) | Ball Mill logic and control | FALSE | TRUE |  | FALSE
BM_RUN_201 | Ball Mill | input/output | Ball Mill logic and indication of ball mill state output PVFL BMRUN201 indicates status RUNNING/NOT RUNNING | FALSE | TRUE |  | FALSE
BM_TANK | Ball Mill Tank | none (logic only) | BMT logic; contains blocks to perform program execution relevent to ball mill page of HMI (304) | FALSE | TRUE |  | FALSE | part of Joshua Dring's thesis
BM_TANK_OP | Ball Mill Tank | input/output | cycles the valves, motors, and pumps present on pg 303 of the HMI | FALSE | TRUE |  | TRUE | Automation SCM, part of Joshua Dring's thesis
BMP_FLT_241 | Ball Mill Pump | input | indication of fault status of mall mill pump output PVFL BMPFLT241 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
BMP_OFF_241 | Ball Mill Pump | input/output | ball mill pump status logic, determines if BMP is on or off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of BMP, BMT level, and CUFT level.
BMP_REF_241-R1A | Ball Mill Pump | none (logic only) | ball mill pump speed reference control. (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
BMP_REF_241_MNTC | Ball Mill Pump | none (logic only) | ball mill pump speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
CA_623 | CSTR1? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CA_643 | CSTR2? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CA_663 | CSTR3? | none (logic only) | unknown (no commenting) conductivity sensors? | FALSE | TRUE | FALSE | FALSE | !!
CM_FF_Test | N/A | N/A | Foundation fieldbus example CM | FALSE | FALSE | FALSE | FALSE | FOUNDATION FIELDBUS EXAMPLE CM
CRP_FLT_341 | Cyclone Recycle Pump | input | indication of fault status of cyclone recycle pump output PVFL CRPFLT341 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
CRP_OFF_341 | Cyclone Recycle Pump | input/output | cyclone recycle pump status logic, determines if CRP is on/off | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks PVs relating to flow out of CRP, 3WV-368 position, supply tank levels, and CUFT level.
CRP_REF_341-R1A | Cyclone Recycle Pump | none (logic only) | CRP speed reference control. (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
CRP_REF_341_MNTC | Cyclone Recycle Pump | none (logic only) | CRP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
CSTR_TANKS | CSTR bank | none (logic only) | CSTR bank logic; contains blocks to perform the program execution relevent to CSTR page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
CSTR_TANKS_OP | CSTR bank | input/output | cycles the valves, motors, and pumps present on pg 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
CUF_TANK | Cyclone Underflow Tank | none (logic only) | CUFT logic, contains blocks to perform the program execution relevent to cyclone page of HMI (306) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
CUF_TANK_OP | Cyclone Underflow Tank | input/output | cycles the valves, pumps, and motors present on og 306 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
CUFP_FLT_361 | Cyclone Underflow Pump | input | indication of fault status of CUFP. Output PVFL CUFPFLT361 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
CUFP_OFF_361 | Cyclone Underflow Pump | input/output | cyclone underflow pump status logic, determines if CUFP is on/off | FALSE | TRUE | TRUE | FALSE | ** Contains configurable interlock PVs relating to flow out of CUFP, BMT lavel, and CUFT level. **possible irrational interlock**
CUFP_REF_361-R1A | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
CUP_REF_361_MNTC | Cyclone Underflow Pump | none (logic only) | CUFP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** inconsistant nomenclature of CUFP vs CUP in other cyclone underflow pump CMs
DP_FLT_611 | Dye Pump | input | Indication of fault status of dye pump output PVFL DPFLT611 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
DP_OFF_611 | Dye Pump | input/output | dye pump status logic, determines if DP IS ON/OFF | FALSE | TRUE | TRUE | FALSE | Contains configurable interlocks relating to DT>CSTR SVs SV_614,615,616, and flow out of DP.
DP_REF_611 | Dye Pump | none (logic only) | DP speed reference control | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_103 | Supply Tank 1 | input | Data acquisition of density transmitter on supply tank 1 | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_123 | Supply Tank 2 | input | Data acquisition of density transmitter on supply tank 2 | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_223 | Ball Mill Tank | input | Data acquisition of density transmitter on ball mill tank | FALSE | TRUE | FALSE | FALSE | Density transmitters
DT_323 | Cyclone Underflow Tank | input | Data acquisition of density transmitter on CUFT | FALSE | TRUE | FALSE | FALSE | Density transmitters
FCV_541-R1A | FCV (NLT input) | output | nonlinear tank input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_541_MNTC | FCV (NLT input) | output | nonlinear tank input FCV control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | ** FCVs inconsistant nomenclature with other maintenance mode controls
FCV_570-R1A | FCV (NT to CSTR1) | output | needle tank to cstr1 FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_571-R1A | FCV (NT to STs) | output | Needle tank to supply tanks FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_574-R1A | FCV (NT to BM) | output | needle tank to ball mill FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_622-R1A | FCV (Steam to CSTR1) | output | CSTR1 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_642-R1A | FCV (Steam to CSTR2) | output | CSTR2 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_662-R1A | FCV (Steam to CSTR3) | output | CSTR3 steam input FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_688-R1A | FCV (Prod. From PP) | output | product output (from CSTR3 PP) FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FCV_690-R1A | FCV (Reflux from PP) | output | reflux from CSTR3 to CSTR1,2,3 FCV control (Controller MV) | FALSE | TRUE | TRUE | FALSE | Part of 2022 MUPP Controller Revision
FDP_FLT_521 | Flow Disturbance Pump | input | indication of fault status of flow disturbance pump output PVFL FDPFLT521 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
FDP_OFF_521 | Flow Disturbance Pump | input/output | flow disturbance pump status logic, determines if FDP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FDP, NT level and NLT level.
FDP_REF_521-R1A | Flow Disturbance Pump | none (logic only) | FDP speed reference control | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
FDP_REF_521_MNTC | Flow Disturbance Pump | none (logic only) | FDP speed reference control (Alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
FP_FLT_141 | Feed Pump | input | indication of fault status of feed pump output PVFL FPFLT141 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
FP_OFF_141 | Feed Pump | input/output | feed pump status logic, determines if FP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlocks relating to flow out of FP, supply tank 1 level and supply tank 2 level.
FP_REF_141-R1A | Feed Pump | none (logic only) | FP speed reference control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
FP_REF_141_MNTC | Feed Pump | none (logic only) | FP speed reference control (Alternative) Maintenance mode | FALSE | TRUE | FALSE | FALSE | **
FT_148 | FT (FP to BM) | input | feed pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_247 | FT (BMP to Cyclone) | input | ball mill pump to hydrocyclone flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_347 | FT (CRP to BM) | input | cyclone recycle pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_363 | FT (CUFP to STs) | input | cyclone underflow pump to storage tanks flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable !!! Possible mistake on Hopkinson P&ID, unable to determin if FT_363 is CUFP to STs, or CRP to BM
FT_401 | FT (Lamella to NT) | input | lamella overflow to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_523 | FT (FDP to NT) | input | flow disturbance pump to needle tank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_569 | FT (NUFP to CSTR1) | input | needle tank underflow pump to cstr1 flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_573 | FT (NUFP to BM) | input | needle tank underflow pump to ball mill flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
FT_613 | FT (DP to CSTR bank) | input | dye pump to cstr bank flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
FT_687 | FT (PP to Output) | input | product pump to output drain flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented, appears to be also doing some kind of conversion from read value to a separate outputted variable
FT_689 | FT (PP to CSTR reflux) | input | product pump to cstr reflux piping flow transmitter read | FALSE | TRUE | FALSE | FALSE | uncommented
I/O | N/A | N/A | input/output read/write? | FALSE | TRUE | FALSE | FALSE
LT_102 | LT (Storage Tank 1) | input | storage tank 1 level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_122 | LT (Storage Tank 2) | input | storage tank 2 level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_222 | LT (BMT) | input | Ball mill tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_322 | LT (CUFT) | input | cyclone underflow tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_422 | Bool (LL/HH) Lamella? | input | unknown (no commenting), presumed to be lamella LL and HH sensors. See use in LUP_OFF_421 | TRUE | FALSE | FALSE | FALSE | !!
LT_501 | LT (NT) | input | needle tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_542 | LT (NLT) | input | nonlinear tank level transmitter read | FALSE | TRUE | FALSE | FALSE
LT_667 | LT (CSTR3) | input | cstr3 tank level treansmitter read | FALSE | TRUE | FALSE | FALSE
LUP_FLT_421 | Lamella underflow pump | input | indication of fault status of lamella underflow pump output PVFL LUPFLT421 indicates FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
LUP_OFF_421 | Lamella underflow pump | output | lamella underflow pump status logic, determines if LUP is on/off | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to lamella LL alarm
LUP_REF_421-R1A | Lamella underflow pump | none (logic only) | LUP reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
LUP_RUN_421 | Lamella underflow pump | input | indication of LUP state output PVFL LUPRUN421 indicates status ON/OFF | TRUE | FALSE | FALSE | FALSE
MAINTENANCE | N/A | N/A | Part of automated maintenance program, storage of SCM PVs/PVFLs | FALSE | FALSE | FALSE | FALSE | variable storage for SCMs, part of Dring's thesis
MS_100 | Maintenance Switch | input | Maintenance switch read, activates maintenance mode output PVFL MS_100 pulses to initiate MM | FALSE | TRUE | FALSE | FALSE | more or less indicate only, activates Dring's maintenance mode
NT_TANKS | NLT/NT | none (logic only) | contains logic to perform execution of program related to NT page | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis comments say related to cyclone page (305) however logic indicates its related to NT/NLTs
NT_TANKS_OP | NLT/NT | none (logic only) | cycles the valves, pumps, and motors present on og 305 of the HMI | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
NTP_FLT_561 | Needle Tank Underflow Pump | input | indication of fault status of needle tank underflow pump output PVFL NTPFLT561 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
NTP_OFF_561 | Needle Tank Underflow Pump | input/output | needle tank underflow pump state logic, determines if NTP is on/off | FALSE | TRUE | TRUE | FALSE | **contains configurable interlocks relating to flow from NTP to BMT and CSTR1, NT Level, CSTR3 level **possible irrational interlock**
NTP_REF_561-R1A | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
NTP_REF_561_MNTC | Needle Tank Underflow Pump | none (logic only) | needle tank underflow pump reference speed control (alternative) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
OneWireless_CM | N/A | N/A | Handles Wireless comms with Honeywell VIA Modbus TCP/IP | FALSE | TRUE | FALSE | FALSE | wireless comms
OPERATION | N/A | N/A | Uncommented, cruicial to plant operation, allows on state of all pumps, sv's, agitators etc. | FALSE | TRUE | FALSE | FALSE | !!
PC3_11_WD1 | N/A | N/A | unknown (uncommented) | FALSE | FALSE | FALSE | FALSE | !!! Possibly unused
PID10_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID10_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID11_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID11_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID12_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID12_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID13_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID13_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID14_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID14_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID15_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID15_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID16_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID16_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID17_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID17_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID18_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !!
PID19_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID19_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID1_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID1_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID20_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !!
PID2_PV_SELECT | N/A | N/A | Spare PV routing, not needed for 2022 controller update | FALSE | TRUE | FALSE | FALSE | !!
PID3_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID3_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID4_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID4_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID5_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID5_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID6_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID6_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID7_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID7_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID8_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID8_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID9_PV_SELECT-R1A | N/A | N/A | PV1, PV2, DV routing for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID9_AutVar_SELECT-R0A | N/A | N/A | Checking for if PV1, PV2 selected on HMI is in use by another controller | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PID_PvSp_ARRAY-R1A | N/A | N/A | Stores variable arrays for control system | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PP_FLT_681 | Product Pump | input | indication of fault status of product pump output PVFL PPFLT681 indicates fault status FAULT/NO FAULT | TRUE | FALSE | FALSE | FALSE
PP_OFF_681 | Product Pump | input/output | product pump state logic, determines if PP is on/off | FALSE | TRUE | TRUE | FALSE | ** contains configurable interlocks relating to flow out of PP via FT_687,689, CSTR3 level, and a combined valve limit imposed on FCV_688,690. **possible irrational interlock**
PP_REF_681-R1A | Product Pump | none (logic only) | Product pump reference speed control (Controller MV) | FALSE | TRUE | FALSE | FALSE | Part of 2022 MUPP Controller Revision
PP_REF_681_MNTC | Product Pump | none (logic only) | Product pump reference speed control (Alternatice) Maintenance Mode | FALSE | TRUE | FALSE | FALSE | **
PPSTLevels1__WD1 | N/A | N/A | unknown (uncommented) |  |  |  |  | !!! Possibly unused
PT_669 | Steam Pressure Trans. | input | Data Acquisition for pressure transmitter on steam line | FALSE | TRUE | FALSE | FALSE
SPARE | N/A | none (logic only) | Labelled as spare PID action control flow | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
ST_TANKS | Storage Tanks | none (logic only) | contains logic to perform execution of program related to Storage tank page (302) | FALSE | TRUE | FALSE | FALSE | part of Joshua Dring's thesis
ST_TANKS_OP | Storage Tanks | none (logic only) | cycles the valves, motors and pumps associated with first section of the plant (HMI pp 302) | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
SV_104 | Storage Tank 1 | output | SV from water addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level
SV_105 | Storage Tank 1 | output | SV from Air addition outlet to storage tank 1 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 1 level
SV_124 | Storage Tank 2 | output | SV from water addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level
SV_125 | Storage Tank2 | output | SV from Air addition outlet to storage tank 2 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to storage tank 2 level
SV_614 | CSTR3 | output | SV from dye pump to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level
SV_615 | CSTR2 | output | SV from dye pump to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_616 | CSTR1 | output | SV from dye pump to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_691 | CSTR3 | output | SV from product pump reflux to CSTR3 | FALSE | TRUE | TRUE | FALSE | contains configurable interlock relating to CSTR3 level
SV_692 | CSTR2 | output | SV from product pump reflux to CSTR2 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_693 | CSTR1 | output | SV from product pump reflux to CSTR1 | FALSE | TRUE | TRUE | FALSE | **contains configurable interlock relating to CSTR3 level
SV_AIR | AIR System | output | Determines if AIR supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
SV_STEAM | STEAM System | output | Determines if STEAM supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
SV_WATER | WATER System | output | Determines if WATER supply solenoid is open/closed | FALSE | TRUE | FALSE | FALSE | ** Not sure if this SV exists, need to find out
TempPC1_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2_2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2OP3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TempPC2OP_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC4_3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC5_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLevPC6_0_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TmpLvlPC3_WD1 | N/A | N/A | unknown (uncommented) | FALSE | TRUE | FALSE | FALSE | !!! Possibly unused
TRBSHT_OP | System Control | none (logic only) | Changes all mode attributes of each device control to program | FALSE | TRUE | FALSE | TRUE | Automation SCM, part of Joshua Dring's thesis
TT_568 | CSTR1 | input | Data Acquisition from temperature transmitter on CSTR1 feed inlet | FALSE | TRUE | FALSE | FALSE
TT_623 | CSTR1 | input | Data Acquisition from temp trans. Inside CSTR1 | FALSE | TRUE | FALSE | FALSE
TT_643 | CSTR2 | input | Data Acquisition from temp trans. Inside CSTR2 | FALSE | TRUE | FALSE | FALSE
TT_663 | CSTR3 | input | Data Acquisition from temp trans. Inside CSTR3 | FALSE | TRUE | FALSE | FALSE
WARN_BUZZ | Warning Buzzer | output | Control of warning buzzer | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant
WARN_LGHT | Warning Light | input | control of warning light allegedly | FALSE | TRUE | FALSE | FALSE | ** investigate further, reference in Pol's thesis of these being redundant